## Data Center Power Requirements
No. | Item | Data Required | Calculation | Input | Subtotal kW
Power Requirement - Electrical | [5 empty] | Please Choose
1 | Critical Load - Sizing calcualtor value from APC website | Rating of each IT Device | (Calculator Total in VA x 0.67)/1000 | 0 | 0 | Yes
2 | For Equipment not listed in the sizing calculator, critical load - nameplate | Subtotal VA (include fire, security and monitoring systems) | (Subtotal VA x 0.67)1000 | 0 | 0 | No
3 | Future Loads | VA of nameplate of each anticipated IT device | [(Add VA rating of future devices) x 0.67]/1000 | 0 | 0
4 | Peak power draw due to variation in cirtical loads | Total steady state critical load power draw | (#1+#2+#3)x1.05 |  | 0
5 | UPS Inefficiency and battery charging | Actual Load + Future Loads (in kW) | (#1+#2+#3)x0.32 |  | 0
6 | Lighting | Total Floor area associated with the data center | 0.0215 x floor area (sq m) | 0 | 0
| Lighting | Total Floor area associated with the data center | 0.002 x floor area (sq ft) | 0 | 0
7 | Total Power to support electrical demands | Total from #4,#5, and #6 above | #4+#5+#6 |  | 0
Power Requirement - Cooling
8 | Total power to support cooling demands | Total from #7 above | For Chiller systems #7 x.07 | Please Choose | 0
| Total power to support cooling demands | Total from #7 above | For DX systems #7 x 1.0 | Please Choose | 0
Total Power Requirement
9 | Total power to support electrical and cooling demands | Total from #7 and #8 above | #7+#8 |  | 0
Size of Electrical Service Estimate
10 | Requirements to meet NEC and other regulators | Total from #9 above | #9 x 1.25 |  | 0
11 | Three phase AC voltage provided at service entrance | AC Voltage |  | 0 | 0.57803
| Electrical servie required from utility company in Amps | Total from #10 and AC voltage in #11 | (#10 x 1000)/(#11 x 1.73) |  | 0
Size of Standby Generator Estimate (If Applicable)
12 | Critical loads requireing generator backup | Total from #7 above | #7 x 1.3, power factor corrected UPS | Please Choose | 0
| Critical loads requireing generator backup | Total from #7 above | #7 x 3.0, double conversion UPS | Please Choose | 0
13 | Cooling loads requiring generator backup | Total from #8 above | #8 x 1.5 |  | 0
14 | Size of generator needed | Total from #12 and #13 above | #12 + #13 |  | 0
This calculator was built using APC formulas taken from the below reference by Jered McClure, please ensure that any reference to this calculator references the below white paper. Richard Sawyer(2004) Calculating Total Power Requirements for Data Centers, White Paper #3, http://www.gocsc.com/uploads/white_papers/1C360F8416E4436C86B8C0874E65BE5E.pdf

## UPS Requirements
Total UPS Requirements
No of UPS Units | Total kVA | Per UPS kVA | Recommended UPS kVA
1 | 0 | 0 | 0 | kVA
Day 1 UPS Requirements
No of UPS Units | Total kVA | Per UPS kVA | Recommended UPS kVA
1 | 0 | 0 | 0 | kVA

## Estimated Running Costs
Total Electrical Costs
Input | [5 empty] | Five Day Week
Energy Tariff Rate (Cents) | Hours Run Per Day | Fixed Charges (cents daily) | kVA | Hourly Running Costs | Daily Running Costs | Weekly Running Costs | Fortnightly Running Costs | Monthly Running Costs | Quarterly Running Costs | Bi-Annual Running Costs | Yearly Costs
27.785 | 24 | 99.559 | 0 | 0 | 0.99559 | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182
Notes Area (press alt + enter to go to the next line): | [5 empty] | Seven Day Week
[6 empty] | Weekly Running Costs | Fortnightly Running Costs | Monthly Running Costs | Quarterly Running Costs | Bi-Annual Running Costs | Yearly Costs
[6 empty] | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182
Estimated Median Costs
[6 empty] | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182
Day 1 Electrical Costs
Day 1 Values | [5 empty] | Five Day Week
Energy Tariff Rate (Cents) | Hours Run Per Day | Fixed Charges (cents daily) | kVA | Hourly Running Costs | Daily Running Costs | Weekly Running Costs | Fortnightly Running Costs | Monthly Running Costs | Quarterly Running Costs | Bi-Annual Running Costs | Yearly Costs
27.785 | 24 | 99.559 | 0 | 0 | 0.99559 | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182
Notes Area (press alt + enter to go to the next line): | [5 empty] | Seven Day Week
[6 empty] | Weekly Running Costs | Fortnightly Running Costs | Monthly Running Costs | Quarterly Running Costs | Bi-Annual Running Costs | Yearly Costs
[6 empty] | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182
Estimated Median Costs
[6 empty] | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182
Year 1 Median Costs
[6 empty] | Weekly Running Costs | Fortnightly Running Costs | Monthly Running Costs | Quarterly Running Costs | Bi-Annual Running Costs | Yearly Costs
[6 empty] | 6.9691 | 13.9383 | 27.8765 | 83.6296 | 167.2591 | 334.5182